## Trace Matrix
Requirement ID | Requirement | Category | Criticality | Recommended Verification | DQ | FAT | SAT | Commissioning | IQ | OQ | PQ | Verified | Verified By
URS-001 | The occupant limit for the pre-gown room (606) shall be 1 personnel. | Occupancy Control | High | Ensure compliance with occupancy limits to maintain controlled environment integrity. | TEST-001 |  |  | TEST-002 | TEST-003 |  |  | Yes | OQ-001
URS-002 | The occupant limit for the gown room (607) shall be 1 personnel. | Facility Design and Control | High | Ensure compliance with gowning procedures and personnel limits. | TEST-004 |  | TEST-005 | TEST-006 | TEST-007 | TEST-008 | TEST-009 | No
URS-003 | The occupant limit for the clean room (609) shall be 2 personnel. | Clean Room Occupancy | Medium | Ensure compliance with occupancy limits during operations. | TEST-010 |  |  | TEST-011 | TEST-012 |  |  | No
URS-004 | The occupant limit for the equipment drying pass room (610) shall be 1 personnel. | Occupancy Limit | High | Monitoring of personnel access and occupancy in the drying pass room. | TEST-013 |  | TEST-014 | TEST-015 | TEST-016 | TEST-017 | TEST-018 | Yes
URS-005 | The occupant limit for the equipment pass through room (611) shall be 1 personnel. | Facility Design Requirement | Medium | Ensure compliance with occupancy limits during operational procedures. | TEST-019 |  |  | TEST-020 | TEST-021 |  | TEST-022 | No
URS-006 | Supply side ventilation to classified cleanroom suites shall have terminal HEPA filtration installed, capable of | HVAC System Design | High | HEPA filter integrity testing and airflow validation | TEST-023 |  | TEST-024 | TEST-025 | TEST-026 | TEST-027 | TEST-028 | No
URS-007 | The system shall maintain non-viable airborne particulate conditions within Grade C and Grade D (per EU | Environmental Control | High | Monitoring and testing of airborne particulate levels in Grade C and Grade D areas. | TEST-029 |  | TEST-030 | TEST-031 |  | TEST-032 | TEST-033 | Yes
URS-008 | The system shall maintain viable airborne particulate conditions within Grade C and Grade D (per EU GMP | Environmental Control | High | Monitoring and testing of airborne particulate levels in Grade C and Grade D areas. | TEST-034 |  | TEST-035 | TEST-036 |  | TEST-037 | TEST-038 | No
URS-009 | The system shall maintain the air changes per hour according to Appendix C. | Environmental Control | High | Monitoring and recording of air changes per hour (ACH) must be implemented and validated. | TEST-039 |  | TEST-040 | TEST-041 |  | TEST-042 | TEST-043 | No
URS-010 | The washroom suite shall be clearly labeled. | Labeling and Identification | High | Visual inspection and documentation review | TEST-044 |  |  | TEST-045 | TEST-046 |  |  | Yes
URS-011 | Utility connections requiring less frequent use shall sit within 72” from the floor. | Utility Connection Design | Medium | Visual inspection and measurement of utility connections' height from the floor. | TEST-047 | TEST-048 | TEST-049 | TEST-050 | TEST-051 | TEST-052 | TEST-053 | No
URS-012 | All rooms shall be equipped with a fire protection system. | Safety and Compliance | High | Fire protection system functionality and compliance with local regulations. | TEST-054 | TEST-055 | TEST-056 | TEST-057 | TEST-058 | TEST-059 |  | No
URS-013 | All cleanroom light fixtures shall be enclosed to be protected against the elements in the room. | Cleanroom Environment Control | High | Visual inspection and functional testing of light fixtures to ensure they are properly enclosed and operational. | TEST-060 |  |  | TEST-061 | TEST-062 |  | TEST-063 | Yes
URS-014 | The Decontamination Washer Suite shall include the CNC Washroom (Room 605). | Cleaning Validation | High | Cleaning validation must confirm the effectiveness of the decontamination process for all product contact equipment in the CNC Washroom. | TEST-064 |  |  | TEST-065 | TEST-066 |  | TEST-067 | No
URS-015 | The Decontamination Washer Suite shall include the Pre-Gown Room (Room 606). | Facility Design | High | Ensure that the Pre-Gown Room is designed to prevent contamination and facilitate proper gowning procedures. | TEST-068 |  | TEST-069 | TEST-070 | TEST-071 | TEST-072 | TEST-073 | No
URS-016 | The Decontamination Washer Suite shall include the Gown Room (Room 607). | Facility Design and Equipment | High | Ensure that the Decontamination Washer Suite, including the Gown Room, is designed to prevent cross-contamination and maintain cleanliness. | TEST-074 |  |  | TEST-075 | TEST-076 |  | TEST-077 | Yes
URS-017 | The Decontamination Washer Suite shall include the Utility Room (Room 608). | Facility Design and Utilities | High | Ensure that the Utility Room (Room 608) is designed and equipped to support the decontamination process effectively. | TEST-078 | TEST-079 | TEST-080 | TEST-081 | TEST-082 | TEST-083 | TEST-084 | No
URS-018 | The Decontamination Washer Suite shall include the Glassware Package (Room 609). | Cleaning Validation | High | Cleaning validation must confirm the effectiveness of the decontamination process for the Glassware Package in Room 609. | TEST-085 |  |  | TEST-086 | TEST-087 |  | TEST-088 | No
URS-019 | The Decontamination Washer Suite shall include the Equipment Drying Room (Room 610). | Cleaning and Decontamination | High | Cleaning validation must confirm the effectiveness of the decontamination process for all product contact equipment. | TEST-089 |  |  | TEST-090 | TEST-091 |  | TEST-092 | Yes
URS-020 | The Decontamination Washer Suite shall include the Equipment Pass Through (Room 611). | Cleaning and Decontamination | High | Cleaning validation must be performed to confirm the effectiveness of the decontamination process for the Equipment Pass Through. | TEST-093 |  |  | TEST-094 | TEST-095 |  | TEST-096 | No
URS-021 | The Decontamination Washer Suite shall include the CNC Clean Storage Room (Room 612). | Cleaning Validation | High | Cleaning validation must confirm the effectiveness of the cleaning procedure for all product contact equipment, including the CNC Clean Storage Room. | TEST-097 |  |  | TEST-098 | TEST-099 |  | TEST-100 | No
URS-022 | The unloading chamber door for the decontamination washer shall be accessible. | Accessibility and Maintenance | Medium | Visual inspection and functional testing of the unloading chamber door to ensure it is accessible and operational. | TEST-101 |  |  | TEST-102 | TEST-103 |  | TEST-104 | Yes
URS-023 | The Decontamination Washer Suite shall have minimized dead spaces such as joints, crevices, and cavities in which the product or moisture can settle and lead to cross-contamination or germination. | Design Requirement | High | Visual inspection and cleaning validation protocols should confirm the absence of dead spaces. | TEST-105 |  |  | TEST-106 | TEST-107 |  | TEST-108 | No
URS-024 | All cleanroom elements, components and exposed surfaces shall be designed in such a way that the surfaces are level and smooth. | Design Requirement | High | Visual inspection and surface testing for smoothness and levelness. | TEST-109 |  |  | TEST-110 | TEST-111 |  | TEST-112 | No
URS-025 | All cleanroom elements, components and exposed surfaces shall be designed in such a way that the surfaces are airtight or sealed. | Design Requirement | High | Design review and testing for airtightness and sealing integrity. | TEST-113 |  |  | TEST-114 | TEST-115 |  |  | Yes
URS-026 | All cleanroom elements, components and exposed surfaces shall be designed in such a way that the surfaces are free of protruding sharp edges. | Design Requirement | High | Design review and inspection of cleanroom elements and surfaces. | TEST-116 |  |  | TEST-117 | TEST-118 |  |  | No
URS-027 | All cleanroom elements, components and exposed surfaces shall be designed in such a way that the surfaces are non-particulate generating under normal conditions with regular maintenance. | Design Requirement | High | Design reviews and surface testing for particulate generation. | TEST-119 |  |  | TEST-120 | TEST-121 |  |  | No
URS-028 | The rooms shall have a boundary that distinguishes between higher and lower classification. | Facility Design | High | Design Qualification (DQ) to confirm that the room boundaries are appropriately defined and compliant with classification requirements. | TEST-122 | TEST-123 | TEST-124 | TEST-125 | TEST-126 | TEST-127 |  | Yes
URS-029 | The surfaces of the cleanroom and components shall be resistant against Bachem approved cleaning solutions and sanitizing agents. | Cleaning and Sanitization | High | Surface material testing against Bachem approved cleaning solutions and sanitizing agents. | TEST-128 |  |  | TEST-129 | TEST-130 |  | TEST-131 | No
URS-030 | Clean room walls shall be dry wall. | Facility Design | Medium | Visual inspection and documentation of installation. | TEST-132 |  |  | TEST-133 | TEST-134 |  | TEST-135 | No
URS-031 | Ceiling panels shall have the same engineered features as the wall panels, with pre-cut openings able to accommodate the installation of light fixtures, HEPA filters, etc. | Facility Design | Medium | Ensure that ceiling panels are designed and manufactured to the same specifications as wall panels, including pre-cut openings. | TEST-136 |  |  | TEST-137 | TEST-138 |  |  | Yes
URS-032 | All joints shall be flush, smooth and cleanable. | Design Requirement | High | Visual inspection and cleaning validation | [6 empty] | TEST-139 | No
URS-033 | All corners between walls and from walls to permanent equipment fixtures in the space shall be coved. | Facility Design | High | Visual inspection and measurement of coved corners | TEST-140 |  |  | TEST-141 | TEST-142 |  |  | No
URS-034 | All wall surfaces (including joints, seals, etc.) shall not emit particulates. | Environmental Control | High | Visual inspection and particulate monitoring | TEST-143 |  | TEST-144 | TEST-145 | TEST-146 | TEST-147 | TEST-148 | Yes
URS-035 | All circuits entering and leaving shall be provided with grounding. | Electrical Safety | High | Visual inspection and testing of grounding connections | TEST-149 | TEST-150 | TEST-151 | TEST-152 | TEST-153 | TEST-154 | TEST-155 | No
URS-036 | The clearance height from the floor to the bottom of the clean room suspended ceiling shall be a minimum of 8ft. | Facility Design | High | Measurement of clearance height from the floor to the bottom of the clean room suspended ceiling. | TEST-156 |  |  | TEST-157 | TEST-158 |  |  | No
URS-037 | The cleanroom light fixtures shall be installed flush with the ceiling. | Facility Design | High | Visual inspection and cleaning validation of the area around the light fixtures. | TEST-159 |  |  | TEST-160 | TEST-161 |  | TEST-162 | Yes
URS-038 | Light fixtures which are suitable for cleanroom operations shall be resistant against humidity. | Equipment | High | Testing for humidity resistance and compliance with cleanroom standards. | TEST-163 |  | TEST-164 | TEST-165 | TEST-166 | TEST-167 | TEST-168 | No
URS-039 | All floors shall be coated with a static-dissipative epoxy. | Facility Design | High | Visual inspection and testing of static-dissipative properties. | TEST-169 |  |  | TEST-170 | TEST-171 |  |  | No
URS-040 | Coving shall be provided on wall connections. | Facility Design | Medium | Visual inspection and measurement of coving installation. | TEST-172 |  |  | TEST-173 | TEST-174 |  | TEST-175 | Yes
URS-041 | The total coving piece shall rise up at least 2”. | Design Requirement | Medium | Physical measurement of the coving piece to ensure it rises at least 2 inches. | TEST-176 |  |  | TEST-177 | TEST-178 |  |  | No
URS-042 | The coving radius shall be 1 to 1.25”. | Facility Design | Moderate | Visual inspection and measurement of coving radius | TEST-179 |  |  | TEST-180 | TEST-181 |  |  | No
URS-043 | Doors shall be 1- or 2-winged, with three door hinges and without a door saddle. | Facility Design | Medium | Visual inspection and functional testing of door operation. | TEST-182 |  |  | TEST-183 | TEST-184 |  |  | Yes
URS-044 | Every clean room door shall have an automatic door lock and shall be equipped with a window. | Facility Design | High | Visual inspection and functional testing of the automatic door lock and window integrity. | TEST-185 |  |  | TEST-186 | TEST-187 |  |  | No
URS-045 | All doors shall be equipped with an elastic door frame seal installed circumferentially on three sides. | Facility Design and Maintenance | Medium | Visual inspection and functional testing of door seals. | TEST-188 |  |  | TEST-189 | TEST-190 |  |  | No
URS-046 | Sealing with the floor shall be achieved with a drop-down seal. | Equipment Qualification | High | The drop-down seal must be verified for its effectiveness in maintaining the integrity of the packaging. | TEST-191 |  | TEST-192 | TEST-193 | TEST-194 | TEST-195 | TEST-196 | Yes
URS-047 | The doors shall be adapted to the adjacent cleanroom walls. | Facility Design | High | Visual inspection and measurement of door fit and sealing against cleanroom walls. | TEST-197 |  | TEST-198 | TEST-199 | TEST-200 | TEST-201 | TEST-202 | No
URS-048 | The doors shall be installed flushed to the adjacent cleanroom walls. | Design Requirement | High | Visual inspection and measurement to ensure doors are flush with adjacent cleanroom walls. | TEST-203 |  |  | TEST-204 | TEST-205 |  |  | No
URS-049 | The gap between the bottom of the door and the top edge of the finished floor shall be between 3 and 5 mm. | Facility Design | Medium | Measurement of the gap using appropriate tools (e.g., calipers or gap gauges) to ensure compliance with specified dimensions. | TEST-206 |  |  | TEST-207 | TEST-208 |  |  | Yes
URS-050 | The door from the CNC Washroom to the first airlock (Gowning Room 606) shall be accessed by authorized personnel (align with existing security system). | Access Control | High | Access logs and authorization lists should be reviewed to ensure compliance with access control requirements. | TEST-209 | TEST-210 | TEST-211 | TEST-212 | TEST-213 | TEST-214 |  | No
URS-051 | The interior doors of the gowning airlock and the material/equipment airlock shall be interlocked. | Safety and Compliance | High | Interlock functionality must be tested to ensure that doors cannot be opened simultaneously. | TEST-215 | TEST-216 | TEST-217 | TEST-218 | TEST-219 | TEST-220 |  | No
URS-052 | After opening one door, the subsequent doors shall be interlocked. | Safety and Security | High | Interlock functionality must be tested to ensure that subsequent doors cannot be opened until the previous door is closed. | TEST-221 | TEST-222 | TEST-223 | TEST-224 | TEST-225 | TEST-226 |  | Yes
URS-053 | Once all doors are closed, a differential pressure setpoint shall come into range before another door shall be opened. | Operational Control | High | Ensure that differential pressure setpoint is achieved before door operation. | TEST-227 |  | TEST-228 | TEST-229 | TEST-230 | TEST-231 | TEST-232 | No
URS-054 | All doors shall be equipped with panic locks as required by NFPA and building code. | Safety and Security | High | Ensure panic locks are installed and functional as per NFPA and building code requirements. | TEST-233 |  |  | TEST-234 | TEST-235 |  |  | No
URS-055 | The doors shall be unlocked via a tamper-proof emergency push button (on both sides of the escape door). | Safety and Security | High | Ensure that the emergency push button is tamper-proof and functions correctly from both sides of the escape door. | TEST-236 |  |  | TEST-237 | TEST-238 |  |  | Yes
URS-056 | The opening of all doors shall also work in the event of a power outage. | Operational Continuity | High | Functional testing during power outage scenarios to ensure doors can be opened manually or through backup systems. | TEST-239 |  |  | TEST-240 | TEST-241 |  |  | No
URS-057 | The airlock control components shall be visible from the cleanroom wall. | Facility Design | Medium | Visual inspection of airlock control components from the cleanroom wall to ensure cleanliness and functionality. | TEST-242 |  |  | TEST-243 | TEST-244 |  | TEST-245 | No
URS-058 | Piping routes inside the cleanroom area shall be kept short and installed vertically wherever possible. | Design Requirement | High | Ensure that piping routes are designed and installed according to the specified requirements. | TEST-246 |  |  | TEST-247 | TEST-248 |  |  | Yes
URS-059 | When needed, brackets shall be used such that the piping is kept away from the wall. | Equipment Installation | Medium | Visual inspection and measurement of distance from wall to piping. | TEST-249 |  |  | TEST-250 | TEST-251 |  |  | No
URS-060 | The furniture in the airlocks shall be made of stainless steel where it is possible. | Material Compliance | High | Material specifications and compliance with GMP standards must be verified during design qualification. | TEST-252 |  |  | TEST-253 | TEST-254 |  |  | No
URS-061 | All other fittings shall be cleanroom compatible. | Equipment Compatibility | High | Visual inspection and cleaning validation results. | TEST-255 |  |  | TEST-256 | TEST-257 |  | TEST-258 | Yes
URS-062 | For electrical and signal cables, empty conduits shall be integrated into the wall panels or into the door structures. | Infrastructure and Utilities | Medium | Ensure that conduits are properly integrated to prevent interference with electrical and signal integrity. | TEST-259 | TEST-260 | TEST-261 | TEST-262 | TEST-263 | TEST-264 | TEST-265 | No
URS-063 | All surfaces shall be cleanable (wipe cleaning), flat and smooth, sealed, and abrasion-resistant. | Cleaning and Maintenance | High | Cleaning validation and effectiveness confirmation | TEST-266 |  |  | TEST-267 | TEST-268 |  | TEST-269 | No
URS-064 | The Washroom (Room 605) shall have Purified Water POU. | Utility Qualification | High | Ensure that the Purified Water Point of Use (POU) system meets the specified design and operational requirements. | TEST-270 | TEST-271 | TEST-272 | TEST-273 | TEST-274 | TEST-275 | TEST-276 | Yes
URS-065 | The Glassware Package Room (Room 609) shall have electrical outlets. | Utilities | Medium | Ensure electrical outlets are installed and functioning properly. | TEST-277 | TEST-278 | TEST-279 | TEST-280 | TEST-281 | TEST-282 | TEST-283 | No
URS-066 | Electricity shall be provided in all rooms. | Utility Requirement | High | Ensure consistent and reliable electricity supply to all rooms to support equipment operation and environmental controls. | TEST-284 | TEST-285 | TEST-286 | TEST-287 | TEST-288 | TEST-289 | TEST-290 | No
URS-067 | The light inside the cleanroom and material/gowning airlocks shall be provided with a dedicated light switch inside each space. | Facility Design | Medium | Visual inspection and functional testing of light switches. | TEST-291 |  |  | TEST-292 | TEST-293 |  | TEST-294 | Yes
URS-068 | The clean room area including airlocks shall be provided with low voltage lighting control system. | Facility Design and Control | Medium | The low voltage lighting control system must be verified to ensure it operates effectively within the clean room environment. | TEST-295 |  |  | TEST-296 | TEST-297 |  | TEST-298 | No
URS-069 | All graded rooms shall have a DicksonOne monitoring instrument. | Monitoring Equipment | High | Ensure continuous monitoring of environmental conditions in graded rooms. | TEST-299 | TEST-300 | TEST-301 | TEST-302 | TEST-303 | TEST-304 | TEST-305 | No
URS-001 | The laboratory shall comply with, but not be limited to, the following regulations and guidelines: | Regulatory Compliance | High | Ensure that all electronic records and signatures comply with 21 CFR Part 11 requirements. | TEST-306 | TEST-307 | TEST-308 | TEST-309 | TEST-310 | TEST-311 |  | Yes
URS-002 | UR1 ¦ Laboratory shall be at least 250 square feet and not more than 1000 square feet. ¦ Medium ¦ Provides sufficient space for up to two biosafety cabinets, three incubators, one refrigerator, and adequate bench space while minimizing unnecessary footprint | Facility Design | Medium | Ensure the laboratory space meets the specified dimensions and layout requirements. | TEST-312 |  |  | TEST-313 | TEST-314 |  |  | No
URS-003 | UR2 ¦ Laboratory must 1-2 entrances/exits. ¦ An entrance/exit is required for use of the room. | Facility Design | Medium | Ensure that the design includes 1-2 entrances/exits as specified in the URS. | TEST-315 |  |  | TEST-316 | TEST-317 |  |  | No
URS-004 | UR ¦ Critical activities shall be performed in qualified biosafety cabinets or laminar airflow hoods ¦ High ¦ Ensures appropriate aseptic environments to maintain sample integrity and contamination prevention. | Environmental Control | High | Ensure that biosafety cabinets or laminar airflow hoods are qualified and maintained according to established protocols. | TEST-318 |  | TEST-319 | TEST-320 |  | TEST-321 | TEST-322 | Yes
URS-005 | UR ¦ Room shall ¦ High ¦ Minimizes cross-contamination and supports GMP best practices. | Facility Design | High | Risk assessment and validation of cleaning procedures and HVAC systems. | TEST-323 |  | TEST-324 | TEST-325 | TEST-326 | TEST-327 | TEST-328 | No
URS-006 | UR ¦ Temperature shall be maintained between 15-25°C with monitoring and alarms ¦ Medium ¦ Supports equipment function, personnel comfort, and consistent test conditions. | Environmental Control | Medium | Temperature monitoring system must be validated to ensure it operates within specified limits. | TEST-329 | TEST-330 | TEST-331 | TEST-332 | TEST-333 | TEST-334 | TEST-335 | No
URS-007 | UR ¦ Relative humidity shall be monitored | Environmental Monitoring | High | Continuous monitoring with alarms for deviations | TEST-336 |  | TEST-337 | TEST-338 |  | TEST-339 | TEST-340 | Yes
URS-008 | UR ¦ Ceilings shall be non-porous. ¦ Medium ¦ Prevents harbouring of microbes. | Facility Design | Medium | Visual inspection and microbial testing of surfaces. | TEST-341 |  |  | TEST-342 | TEST-343 |  | TEST-344 | No
URS-009 | UR ¦ Flooring shall be compatible to support the use of detergents and disinfectants that are necessary for cleaning. ¦ High ¦ Facilitates effective cleaning and disinfection. | Facility Design | High | Cleaning validation and effectiveness testing of the flooring material. | TEST-345 |  |  | TEST-346 | TEST-347 |  | TEST-348 | No
URS-010 | UR1 ¦ Door(s) shall be self-closing ¦ Medium ¦ Helps maintain | Facility Design | Medium | Visual inspection and functional testing of door operation. | TEST-349 |  |  | TEST-350 | TEST-351 |  |  | Yes
URS-011 | UR1 ¦ Windows shall be included in doors. ¦ Low ¦ Allows visibility into the lab, reducing unnecessary entry. | Facility Design | Low | Visual inspection of the installed doors to confirm the presence of windows. | TEST-352 |  |  | TEST-353 | TEST-354 |  |  | No
URS-012 | UR1 ¦ Safety signage shall be posted as appropriate ¦ Communicates hazards and required behaviors to personnel. | Safety and Compliance | High | Ensure that safety signage is visible, legible, and appropriately placed in all relevant areas. |  |  |  | TEST-355 |  |  |  | No
URS-013 | UR ¦ Biohazard waste shall be segregated ¦ Medium ¦ Prevents contamination. | Biohazard Waste Management | Medium | Regular audits and inspections of waste segregation practices. |  |  |  | TEST-356 |  |  |  | Yes
URS-014 | UR ¦ Countertops shall be constructed of non-porous, chemical-resistant, and cleanable materials (e.g., epoxy resin, phenolic resin, or stainless steel). ¦ Prevents absorption of contaminants and supports effective cleaning and disinfection. | Material Specification | High | Material testing and cleaning validation | TEST-357 |  |  | TEST-358 | TEST-359 |  | TEST-360 | No
URS-015 | UR ¦ Shelving shall be constructed of cleanable, and designed to minimize dust accumulation (e.g. enclosed cabinets). ¦ Medium ¦ Reduces particulate and microbial contamination risks and supports housekeeping. | Facility Design | Medium | Visual inspection and cleaning validation results. | TEST-361 |  | TEST-362 | TEST-363 |  | TEST-364 | TEST-365 | No